## Corridor
National Load Despatch Centre, New Delhi
Cross Border Transfer Capability for April 2025
Issue Date: 07 November 2024 |  |  | Issue Time: 1500 hrs |  |  |  | Revision No. 3
Cross-Border Corridor | Date | Time Period in IST (hrs) | TTC | Reliability Margin | Available Transfer Capability (ATC) | General Network Access (GNA) | Margin Available for T-GNA | Changes in TTC w.r.t. Last Revision | Limiting constraint | Comments
India (ER ISTS) to Bangladesh * | 1st April 2025 to 30th April 2025 | 00:00-17:00 | 1000 | 0 | 1000 | 982 | 18 |  | Limited to HVDC Bherama-Behrampore rated capacity
|  | 17:00-21:00 | 1000 |  | 1000 | 982 | 18
|  | 21:00-24:00 | 1000 |  | 1000 | 982 | 18
Bangladesh to India (ER ISTS) * | 1st April 2025 to 30th April 2025 | 00:00-17:00 | 1000 | 0 | 1000 | 0 | 1000 |  | Limited to HVDC Bherama-Behrampore rated capacity
|  | 17:00-21:00 | 1000 |  | 1000 | 0 | 1000
|  | 21:00-24:00 | 1000 |  | 1000 | 0 | 1000
India (Tripura) to Bangladesh # | 1st April 2025 to 30th April 2025 | 00:00-17:00 | 200 | - | 200 | 0 | 200 |  | Limited to terminal bay rating at 132 kV Surjamaninagar (TSCL)
|  | 17:00-21:00 | 200 |  | 200 | 0 | 200
|  | 21:00-24:00 | 200 |  | 200 | 0 | 200
Bangladesh to India (Tripura) # | 1st April 2025 to 30th April 2025 | 00:00-17:00 | 200 | - | 200 | 0 | 200 |  | Limited to terminal bay rating at 132 kV Surjamaninagar (TSCL)
|  | 17:00-21:00 | 200 |  | 200 | 0 | 200
|  | 21:00-24:00 | 200 |  | 200 | 0 | 200
India (ER ISTS & NER ISTS) to Bhutan * | 1st April 2025 to 30th April 2025 | 00:00-17:00 | 1100 | 0 | 1100 | 0 | 1100 |  | 1. N-1 of Chukha-Birpara will overload the other circuit 2. Outage of any circuit of 220 kV Birpara - Alipurduar D/C will overload the other circuit, 3. The outage of any one circuit of 220 kV Birpara-Chukha D/C will overload 220 kV Birpara – Malbase 4. Low Voltage in NER system
|  | 17:00-21:00 | 1100 |  | 1100 | 0 | 1100
|  | 21:00-24:00 | 1100 |  | 1100 | 0 | 1100
Bhutan to India (ER ISTS) * | 1st April 2025 to 30th April 2025 | 00:00-17:00 | 2380 | 50 | 2330 | 2185 | 145 |  | N-1 of Chukha-Birpara will overload the other circuit
|  | 17:00-21:00 | 2380 |  | 2330 | 2185 | 145
|  | 21:00-24:00 | 2380 |  | 2330 | 2185 | 145
Bhutan to India (NER ISTS ) * | 1st April 2025 to 30th April 2025 | 00:00-17:00 | 158 | - | 158 | 0 | 158 |  | Limited to loading upto the thermal limit of 132 kV Salaktai-Gelephu & 132 kV Rangia-Motonga
|  | 17:00-21:00 | 158 |  | 158 | 0 | 158
|  | 21:00-24:00 | 158 |  | 158 | 0 | 158
India (Bihar ) to Nepal ## | 1st April 2025 to 30th April 2025 | 00:00-17:00 | 300 | 0 | 300 | 0 | 300 |  | (i) Overloading of 220/132kv, 3x160MVA ICTs at Kishanganj. (ii) Limited to thermal limit of 132 kV Raxual Parwanipur D/C. (iii) Limited to thermal limit of 132 KV Bettiah - Ramnagar, 132 KV Bettia - Thakraha 132 KV Bettiah – Narkatiyaganj lines.
|  | 17:00-21:00 | 300 |  | 300 | 0 | 300
|  | 21:00-24:00 | 300 |  | 300 | 0 | 300
India (NR ISTS) to Nepal * | 1st April 2025 to 30th April 2025 | 00:00-17:00 | 80 | - | 80 | 0 | 80 |  | Limited to ampacity of 132 kV Tanakpur-Mahendranagar S/C line
|  | 17:00-21:00 | 80 |  | 80 | 0 | 80
|  | 21:00-24:00 | 80 |  | 80 | 0 | 80
India (UP ) to Nepal ### | 1st April 2025 to 30th April 2025 | 00:00-24:00 | 50 | 0 | 50 | 0 | 50 |  | Overloading of 132 kV Anand Nagar – New Nautanwa under outage of 132 kV New Nautanwa – Bansi S/C.
Nepal to India (NR ISTS) * | 1st April 2025 to 30th April 2025 | 00:00-17:00 | 80 | 0 | 80 | 0 | 80 |  | Limited to ampacity of 132 kV Tanakpur-Mahendranagar S/C line
|  | 17:00-21:00 | 80 |  | 80 | 0 | 80
|  | 21:00-24:00 | 80 |  | 80 | 0 | 80
India (ER ISTS ) to Nepal * | 1st April 2025 to 30th April 2025 | 00:00-17:00 | 800 | 0 | 800 | 0 | 800 |  | Limited on account of transformation capacity at 400/220 kV Dhalkebar S/s
|  | 17:00-21:00 | 800 |  | 800 | 0 | 800
|  | 21:00-24:00 | 800 |  | 800 | 0 | 800
Nepal to India (ER ISTS ) * | 1st April 2025 to 30th April 2025 | 00:00-17:00 | 800 | 0 | 800 | 0 | 800 |  | Limited on account of transformation capacity at 400/220 kV Dhalkebar S/s
|  | 17:00-21:00 | 800 |  | 800 | 0 | 800
|  | 21:00-24:00 | 800 |  | 800 | 0 | 800
India (Manipur ) to Myanmar # | 1st April 2025 to 30th April 2025 | 00:00-17:00 | 3.4 | - | 3.4 | 0 | 3.4 |  | Limited to loading upto the thermal limit of 11 kV Moreh -Tamu
|  | 17:00-21:00 | 3.4 |  | 3.4 | 0 | 3.4
|  | 21:00-24:00 | 3.4 |  | 3.4 | 0 | 3.4
Myanmar to India (Manipur ) # | 1st April 2025 to 30th April 2025 | 00:00-17:00 | 3.4 | - | 3.4 | 0 | 3.4 |  | Limited to loading upto the thermal limit of 11 kV Moreh -Tamu
|  | 17:00-21:00 | 3.4 |  | 3.4 | 0 | 3.4
|  | 21:00-24:00 | 3.4 |  | 3.4 | 0 | 3.4
Note 1: | In case of operation of SPS, Transfer Capability will be revised accordingly.
Note 2: | Schedule between India and Bangladesh will be prepared using the above table till the next revision
Note 3: | Transfer Capability between India and Bangladesh in the above table has been evaluated ignoring the constraints from Bangladesh side.
Note 4: | Deemed GNA of Bangladesh from India is considered as 300 MW from DVC, 450 MW from Sembcorp Energy India Limited and 232 MW from ISGS allocation (excluding auxiliaries+losses).
Note 5: | * ISTS to cross-border TTC/ATC is for security & market purpose.
Note 6: | # Intra-state to cross-border TTC/ATC is for security purpose only
Note 7: | ## TTC is the sum of individual maximum permissible load as Nepal is fed radially & declared by SLDC Bihar.
Note 8: | ### The transfer capability from UP to Nepal through 132 kV Nautanwa – Mainhiya D/C line
Note 9: | The above limits are considering the network limitation on Indian side. In case cross-border NLDC also declare the TTC/ATC considering the netowrk limitation on their respective side, the lower of this values vs values in above table would be reckoned for the purpose of scheduling.
Note 10 : | In case any other constraint would be intimated by respective cross-border NLDC, these figures would be revised accordingly.
Note 11 : | NLDC India would approve the transactions in line with the GOI guidelines of Dec 2018, CERC Cross Border regulations and the CBTE procedure issued by DA.
http://powermin.nic.in/sites/default/files/uploads/Guidelines_for_ImportExport_Cross%20Border_of_Electricity_2018.pdf
http://www.cercind.gov.in/2019/regulation/CBTE-Regulations2019.pdf
https://cea.nic.in/wp-content/uploads/2021/02/Final_DA_Procedure_26022021.pdf

## Reasons for Revision
Cross Border Transfer Capability for Nov 2024
Revision No | Date of Revision | Period of Revision | Reason for Revision
1 | 30th April 2024 | 1st Nov 2024 to 30th Nov 2024 | Change in LGB and assessment of transfer capability from UP to Nepal through 132 kV Nautanwa – Mainhiya D/C line
2 | 1st Nov 2024 to 30th Nov 2024 | 6th Nov 2024 to 30th Nov 2024 | Change in LGB and assessment of transfer capability from India (ER-ISTS + NER-ISTS) to Bhutan
3 | 7th November 2024 | 8th November 2024 | Due to the shutdown of 220KV MAIN BUS - 1 & 2 AT BIRPARA, 220KV-BIRPARA-MALBASE-1 & 220KV-CHUKHA-BIRPARA-1 & 2